REWARD FUNCTION COMPONENTS AND DESCRIPTIONS

Cost_EnergyImport – Penalizes buying electricity from the grid; higher grid import cost per kWh leads to more negative reward.

Revenue_EnergyExport – Rewards selling excess electricity back to the grid; more export at high price increases positive reward.

Cost_DemandPeak – Penalizes high instantaneous grid power import peaks that could increase demand charges on the electricity bill.

Cost_FuelCellHydrogenUse – Penalizes hydrogen consumption by the fuel cell to reflect the value of stored hydrogen for future emergencies.

Cost_ElectrolyzerEnergyUse – Penalizes energy consumed by the electrolyzer so it does not waste electricity when hydrogen is not needed.

Penalty_UnservedCriticalLoad – Very strong penalty when critical hospital loads are not fully supplied; represents risk to patient safety and must dominate the reward.

Penalty_UnservedNonCriticalLoad – Smaller penalty when non-critical loads are curtailed; this allows controlled load shedding but still discourages unnecessary discomfort.

Penalty_GridOutageViolation – Penalty applied when the microgrid fails to maintain supply during a grid outage despite having theoretical local resources to do so.

Reward_BatterySOC_Stability – Rewards keeping the battery state of charge within a desirable mid-range band, avoiding both deep discharge and overcharge regions.

Penalty_BatteryDeepDischarge – Extra penalty when the battery SOC falls below a critical threshold (e.g., 20%), representing accelerated degradation and risk of blackout.

Penalty_BatteryHighSOC – Penalty when battery SOC stays too close to 100% for long periods, representing stress and lack of usable headroom.

Penalty_BatteryC_Rate – Penalizes very high charge or discharge power relative to capacity (high C-rates), which accelerates battery wear.

Penalty_FuelCellRamping – Penalizes rapid changes in fuel cell power setpoint to avoid thermal and mechanical stress on the stack.

Penalty_ElectrolyzerRamping – Penalizes large power swings in the electrolyzer to prevent efficiency loss and extend stack lifetime.

Penalty_TemperatureLimits – Penalty if any component (battery, fuel cell, electrolyzer, inverter) operates outside its safe temperature band.

Penalty_HydrogenOverfill – Strong penalty when hydrogen tank level approaches or exceeds safe storage capacity.

Reward_HydrogenStrategicReserve – Rewards keeping hydrogen level above a minimum strategic reserve threshold for blackout resilience.

Reward_RenewableUtilization – Rewards using locally generated solar power instead of drawing from the grid, reflecting decarbonization and self-consumption goals.

Penalty_CurtailmentPV – Penalizes curtailing PV generation (turning down solar output) when there is still unserved load or available storage capacity.

Reward_EmissionReduction – Rewards operating modes that correspond to lower CO₂ emissions (e.g., less grid power during high-carbon periods, more use of PV and stored hydrogen).

Penalty_SwitchingFrequency – Penalizes excessively frequent switching of modes (battery charge/discharge, fuel cell on/off, electrolyzer on/off) to avoid wear and control instability.

Penalty_VoltageFrequencyDeviation – Penalty when microgrid bus voltage or frequency deviates outside specified tolerance, representing power quality issues.

Reward_ComfortHVAC – Rewards keeping indoor climate (temperature or inferred comfort) within a comfortable range while still being energy efficient.

Penalty_ConstraintViolation – Generic penalty term that triggers when any hard operational constraint is violated (safety limits, reserve margins, equipment operating envelopes).

Reward_ResilienceScore – Composite reward for meeting resilience objectives during disturbances (grid outage, sudden load spikes, PV drops), e.g., no loss of critical load over an event window.

Reward_PredictionTracking – Rewards the controller when actual system evolution matches its internal forecasts (for load or PV), encouraging actions that reduce forecast error impact.